{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":13,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSSC2"]
[]
[]
[]
[]
["","","","","","EWADH13TZSSC2","EWADH19TZSSC2","EWADH11TZSSC2","EWADH17TZSSC2","EWADH18TZSSC2","EWADH12TZSSC2","EWADC16TZSSC2","EWADC15TZSSC2"]
["Chladiaci výkon","Men.","","","kW","1,355","1,965","1,189","1,766","1,875","1,259","1,644","1,508"]
["Regulácia výkonu","Metóda","","","","Variabilná","Variabilná","Variabilná","Variabilná","Variabilná","Variabilná","Variabilná","Variabilná"]
["","Minimálna kapacita","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Príkon","Chladenie","","Men.","kW","438.6","709.3","380.9","581.8","636.4","413.4","532.8","485"]
["EER","","","","","3.09","2.77","3.12","3.04","2.95","3.05","3.09","3.11"]
["IPLV","","","","","4.78","4.99","4.85","5.07","5.04","4.8","5.11","5.14"]
["SEER","","","","","4.65","4.68","4.69","4.86","4.83","4.64","4.87","4.83"]
["Vonkajšie rozmery","Jednotka","","Hĺbka","mm","11,404","14,102","10,510","13,202","14,102","10,510","12,302","11,404"]
["","","","Výška","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Šírka","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Hmotnosť","Prevádzková hmotnosť","","","kg","11,123","13,048","9,879","12,575","13,048","9,879","12,145","11,727"]
["","Jednotka","","","kg","10,112","12,037","9,322","11,564","12,037","9,322","11,134","10,716"]
["Opláštenie","Farba","","","","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela","Slonovinovo biela"]
["","Materiál","","","","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom","Pozinkovaný oceľový plech s náterom"]
["Výmenník tepla vzduchu","Typ","","","","Mikro kanál","Mikro kanál","Mikro kanál","Mikro kanál","Mikro kanál","Mikro kanál","Mikro kanál","Mikro kanál"]
["Ventilátor","Množ.","","","","24","30","22","28","30","22","26","24"]
["","Typ","","","","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo","Priame čerpadlo"]
["Motor ventilátora","Pohon","","","","Zap./Vyp.","Zap./Vyp.","Zap./Vyp.","Zap./Vyp.","Zap./Vyp.","Zap./Vyp.","Zap./Vyp.","Zap./Vyp."]
["Kompresor","Množstvo_","","","","2","2","2","2","2","2","2","2"]
["","Typ","","","","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom","Skrutkový kompresor riadený invertorom"]
["","Starting method","","","","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD","Poháňaný VFD"]
["Úroveň akustického výkonu","Chladenie","","Men.","dBA","104","107","102","105","106","103","105","104"]
["Hladina akustického tlaku","Chladenie","","Men.","dBA","82","84","80","82","83","81","82","81"]
["Chladivo","Typ","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","200","270","175","250","270","175","220","200"]
["","Obvody","","Množstvo","","2","2","2","2","2","2","2","2"]
["Pripojenia potrubí","Vstup / výstup vody z výparníka (OD)","","","","273","273","219.1","273","273","219.1","273","273"]
["Power supply","Fáza","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frekvencia","","","Hz","50","50","50","50","50","50","50","50"]
["","Napätie","","","V","400","400","400","400","400","400","400","400"]
["","Rozsah napätia","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10"]
["Jednotka","Spúšťací prúd","","Max","A","0","0","0","0","0","0","0","0"]
["","Prevádz. prúd","Chladenie","Nom. ot.","A","733.0","1,149","646.5","962.8","1,044","691.1","884.0","813.9"]
["","","","Max","A","1,027","1,487","913","1,301","1,398","969","1,205","1,165"]
["","Maximálny prúd v zariadení na dimenzovanie vodičov","","","A","1,130","1,636","1,004","1,431","1,538","1,066","1,326","1,282"]