{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Hladina akustického tlaku","Chladenie","","Men.","dBA","44.0","47.7","50.8","51.0"]
["Hydraulické súčiastky","Expanzná nádoba","","Objem","l","8","8","8","8"]
["Prevádzkový rozsah","Strana vzduchu","Chladenie","Min.","°CDB","10","10","10","10"]
["","","","Max.","°CDB","43","43","43","43"]
["","","Kúrenie","Max.","°CDB","25","25","25","25"]
["","","","Min.","°CDB","-25","-25","-25","-25"]
["","Strana vody","Kúrenie","Min.","°CDB","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Max.","°CDB","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Chladenie","Max.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Chladivo","Na okruh","","","kg","3.80","3.80","3.80","3.80"]
["","Na okruh","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Kompresor","Type","","","","Hermeticky uzavretý rotačný invertorový kompresor","Hermeticky uzavretý rotačný invertorový kompresor","Hermeticky uzavretý rotačný invertorový kompresor","Hermeticky uzavretý rotačný invertorový kompresor"]
["","Spôsob spúšťania_","","","","Jednotky s invertorom","Jednotky s invertorom","Jednotky s invertorom","Jednotky s invertorom"]
["","Množstvo_","","","","1","1","1","1"]
["Výmenník tepla vzduchu","Typ","","","","Vysokoúčinný typ s lamelou a trubicou, s integrovaným dochladzovačom","Vysokoúčinný typ s lamelou a trubicou, s integrovaným dochladzovačom","Vysokoúčinný typ s lamelou a trubicou, s integrovaným dochladzovačom","Vysokoúčinný typ s lamelou a trubicou, s integrovaným dochladzovačom"]
["Hmotnosť","Unit","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Chladiace médium","GWP","","","","675.0","675.0","675.0","675.0"]
["","Typ","","","","R-32","R-32","R-32","R-32"]
["","Obvody","","Množstvo","","1","1","1","1"]
["","Control","","","","Elektronický expanzný ventil","Elektronický expanzný ventil","Elektronický expanzný ventil","Elektronický expanzný ventil"]
["Motor ventilátora","Rýchlosť","Chladenie","Men.","ot/min","500","550","650","650"]
["","","Kúrenie","Men.","ot/min","400","450","550","650"]
["Chladiaci výkon","Men.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Vodný výmenník tepla","Objem vody","","","l","2","2","2","2"]
["","Minimálny objem vody v systéme","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Typ","","","","Doskový výmenník tepla","Doskový výmenník tepla","Doskový výmenník tepla","Doskový výmenník tepla"]
["Vstup napájania","Chladenie","","Men.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Kúrenie","","Men.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Úroveň akustického výkonu","Chladenie","","Men.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Vonkajšie rozmery","Unit","","Width","mm","1,380","1,380","1,380","1,380"]
["","","","Hĺbka","mm","460","460","460","460"]
["","","","Height","mm","870","870","870","870"]
["Regulácia výkonu","Method","","","","Variabilný (invertor)","Variabilný (invertor)","Variabilný (invertor)","Variabilný (invertor)"]
["Vykur. priestoru","Priemerné podnebie – výstup vody 55°C","Všeobecné","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (Sezónna účinnosť vykurovania priestoru)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilátor","Prietok vzduchu","Kúrenie","Men.","m³/min","48.0","55.8","70.4","85.0"]
["","","Chladenie","Men.","m³/min","63","70","85","85"]
["Vykurovací výkon","Men.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Kompresor","Spôsob spúšťania_","","","","Invertor","Invertor","Invertor","Invertor"]
["Power supply","Phase","","","","3~","3~","3~","3~"]
["","Frekvencia","","","Hz","50","50","50","50"]
["","Názov","","","","W1","W1","W1","W1"]
["","Napätie","","","V","400","400","400","400"]
["Poznámky","","","","","(1) - Chladenie: EW 12℃; LW 7℃; podmienky prostredia: 35° CDB","(1) - Chladenie: EW 12℃; LW 7℃; podmienky prostredia: 35° CDB","(1) - Chladenie: EW 12℃; LW 7℃; podmienky prostredia: 35° CDB","(1) - Chladenie: EW 12℃; LW 7℃; podmienky prostredia: 35° CDB"]
["","","","","","(2) - Chladenie: EW 23℃; LW 18℃; podmienky prostredia: 35° CDB","(2) - Chladenie: EW 23℃; LW 18℃; podmienky prostredia: 35° CDB","(2) - Chladenie: EW 23℃; LW 18℃; podmienky prostredia: 35° CDB","(2) - Chladenie: EW 23℃; LW 18℃; podmienky prostredia: 35° CDB"]
["","","","","","(3) - Podmienka: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Podmienka: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Podmienka: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Podmienka: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Podmienka: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt = 5 °C)","(4) - Podmienka: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt = 5 °C)","(4) - Podmienka: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt = 5 °C)","(4) - Podmienka: Ta DB/WB 7 °C/6 °C - LWC 45 °C (Dt = 5 °C)"]
["","","","","","(5) - Podľa normy EN14825","(5) - Podľa normy EN14825","(5) - Podľa normy EN14825","(5) - Podľa normy EN14825"]
["","","","","","(6) - V závislosti od prevádzkového režimu, prečítajte si inštalačnú príručku.","(6) - V závislosti od prevádzkového režimu, prečítajte si inštalačnú príručku.","(6) - V závislosti od prevádzkového režimu, prečítajte si inštalačnú príručku.","(6) - V závislosti od prevádzkového režimu, prečítajte si inštalačnú príručku."]
["","","","","","(7) - Viac podrobností nájdete na nákrese prevádzkového rozsahu","(7) - Viac podrobností nájdete na nákrese prevádzkového rozsahu","(7) - Viac podrobností nájdete na nákrese prevádzkového rozsahu","(7) - Viac podrobností nájdete na nákrese prevádzkového rozsahu"]