{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":55,"n_cols":11,"rows_kept":55,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FTXP-N"]
[]
[]
[]
[]
["","","","","","FTXP35N5V1B","FTXP50N2V1B","FTXP60N2V1B","FTXP71N2V1B","FTXP20N5V1B (Archived)","FTXP25N5V1B (Archived)"]
["Vstup napájania","Chladenie","","Men.","kW","0.032","0.029","0.032","0.032","0.019","0.02"]
["","Kúrenie","","Men.","kW","0.032","0.032","0.035","0.035","0.023","0.023"]
["Opláštenie","Farba","","","","Biela","Biela","Biela","Biela","Biela","Biela"]
["Vonkajšie rozmery","Jednotka","","Výška","mm","286","295","295","295","286","286"]
["","","","Šírka","mm","770","990","990","990","770","770"]
["","","","Hĺbka","mm","225","263","263","263","225","225"]
["Hmotnosť","Jednotka","","","kg","9","13.5","13.5","13.5","8.5","8.5"]
["Ventilátor","Prietok vzduchu","Chladenie","Vysoké","m³/min","11.5","16.3","16.8","16.8","9.5","9.7"]
["","","","Stredný","m³/min","8.3","14","14.4","14.4","7.4","7.7"]
["","","","Nízka","m³/min","6.3","11.5","11.8","11.8","5.6","5.8"]
["","","","Tichá prevádzka","m³/min","4.5","8.3","9.2","10.1","4.2","4.2"]
["","","Kúrenie","Vysoké","m³/min","11.5","17.3","17.9","17.9","10.4","10.4"]
["","","Vykurovanie","Stredný","m³/min","9","14.4","15.3","15.3","8.1","8.1"]
["","","Kúrenie","Nízka","m³/min","7","11.8","12.4","12.4","6.2","6.4"]
["","","","Tichá prevádzka","m³/min","5.3","10.4","11","11","5.2","5.2"]
["Akustický výkon","Chladenie","","","dBA","58","59","60","62","55","55"]
["","Vykurovanie","","","dBA","58","61","62","62","55","55"]
["Hladina akustického tlaku","Chladenie","","Vysoké","dBA","43","43","45","46","39","40"]
["","","","Stredný","dBA","34","39","41","42","33","33"]
["","","","Nízka","dBA","27","34","36","37","25","26"]
["","","","Tichá prevádzka","dBA","20","27","30","32","19","19"]
["","Kúrenie","","Vysoké","dBA","40","42","44","45","39","40"]
["","Vykurovanie","","Stredný","dBA","35","38","40","41","34","34"]
["","Kúrenie","","Nízka","dBA","29","33","35","36","28","28"]
["","","","Tichá prevádzka","dBA","21","30","32","33","21","21"]
["Pripojenia potrubia","Kvapalina","","OD","mm","6","6.4","6.4","6.4","6","6"]
["","Plyn","","OD","mm","9.5","12.7","12.7","12.7","9.5","9.5"]
["","Odvod kondenzátu","","","","18","18","18","18","18","18"]
["Control systems","Infrared remote control","","","","ARC480A78","ARC480A53","ARC480A53","ARC480A53"]
["Riadiace systémy","Káblový diaľkový ovládač","","","","BRC944B2, BRC073A1","","","","BRC944B2, BRC073A1","BRC944B2, BRC073A1"]
["Štandardné príslušenstvo","Installation manual","","","","1","1","1","1","1","1"]
["","AAA dry-cell batteries","","","","2","2","2","2","2","2"]
["","General safety precautions","","","","1","","","","1","1"]
["","Operation manual","","","","1","1","1","1","1","1"]
["","Titanium apatite deodorizing filter","","","","1","1","1","1","1","1"]
["","Silver particle filter","","","","1","1","1","1","1","1"]
["","Indoor unit fixing screws","","","","2","2","2","2","2","2"]
["","Infrared remote control","","","","1","1","1","1","1","1"]
["","Mounting plate","","","","1","1","1","1","1","1"]
["","Remote control holder","","","","1","1","1","1","1","1"]
["Napájanie","Názov","","","","","V1","V1","V1"]
["","Fáza","","","","1~","1~","1~","1~","1~","1~"]
["Zdroj napájania","Frekvencia","","","Hz","50","50","50","50","50","50"]
["","Napätie","","","V","220-240","220-240","220-240","220-240","220-240","220-240"]
["Štandardné príslušenstvo","WLAN adapter kit","","","","","1","1","1"]
["Riadiace systémy","Infra. diaľkové ovládanie","","","","","","","","ARC480A78","ARC480A78"]
["Poznámky","","","","","","","","","(1) - Chladenie: vnútorná teplota 27°CDB, 19°CWB; vonkajšej teplote 35 °CDB; ekvivalentná dĺžka potrubia: 5m; výškový rozdiel: 0m","(1) - Chladenie: vnútorná teplota 27°CDB, 19°CWB; vonkajšej teplote 35 °CDB; ekvivalentná dĺžka potrubia: 5m; výškový rozdiel: 0m"]
["","","","","","","","","","(2) - Kúrenie: vnútorná teplota 20°CDB; vonkajšej teplote 7°CDB, 6°CWB; príslušnej dĺžky potrubia chladiva: 5m (horizontálna)","(2) - Kúrenie: vnútorná teplota 20°CDB; vonkajšej teplote 7°CDB, 6°CWB; príslušnej dĺžky potrubia chladiva: 5m (horizontálna)"]
["","","","","","","","","","(3) - Elektrické údaje nájdete v samostatných nákresoch","(3) - Elektrické údaje nájdete v samostatných nákresoch"]