{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":73,"n_cols":11,"rows_kept":73,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-L"]
[]
[]
[]
[]
["","","","","","RXS20L2V1B","RXS25L2V1B","RXS35L2V1B","RXS42L2V1B","RXS50L2V1B","RXS60L2V1B"]
["Hladina akustického tlaku","Kúrenie","","Vysoké","dBA","47","47","48","48"]
["","Chladenie","","Vysoké","dBA","46","46","48","48"]
["Štandardné príslušenstvo","Vypúšťací uzáver","","","","1","1","","1"]
["","Návod na montáž","","","","1","1","1","1"]
["","Štítok s náplňou chladiva","","","","1","1","1"]
["","Viacjazyčné štítky o fluórovaných skleníkových plynoch","","","","1","1","Viacjazyčné štítky o fluórovaných skleníkových plynoch"]
["Chladiace médium","Charge","","","TCO2Eq","2.1","2.1","2.5","2.7"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","1.0","1.0","1.20","1.3"]
["","Typ","","","","R-410A","R-410A","R-410A","R-410A"]
["Motor ventil.","Rýchlosť","Chladenie","Super nízke","ot/min","780","780","780","790"]
["","","Kúrenie","Super nízke","ot/min","740","740","740","780"]
["Prevádzkový rozsah","Chladenie","Okolitá teplota","Max.","°CDB","46","46","46","46"]
["","","","Min.","°CDB","-10","-10","-10","-10"]
["","Kúrenie","Okolitá teplota","Max.","° CWB","18","18","18","18"]
["","","","Min.","° CWB","-15","-15","-15","-15"]
["Pripojenia potrubia","Úroveň hladiny","IU - OU","Max.","m","","","15"]
["","Dodatočná náplň chladiva","","","kg/m","","","0,020 (pre potrubie s dĺžkou presahujúcou 10m)"]
["Vonkajšie rozmery","Jednotka","","Šírka","mm","765","765","765","765"]
["","","","Hĺbka","mm","285","285","285","285"]
["","","","Výška","mm","550","550","550","550"]
["Kompresor","Typ","","","","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor"]
["Hmotnosť","Jednotka","","","kg","34","34","34","39"]
["Ventilátor","Prietok vzduchu","Kúrenie","Super nízke","cfm","904","904","904","960"]
["","","","Super nízke","m³/min","25.6","25.6","25.6","27.2"]
["","","Chladenie","Super nízke","m³/min","30.1","30.1","30.1","30.6"]
["","","","Super nízke","cfm","1,063","1,063","1,063","1,080"]
["Power supply","Fáza","","","","1~","1~","1~","1~"]
["","Frekvencia","","","Hz","50","50","50","50"]
["","Napätie","","","V","220-240","220-240","220-240","220-240"]
["Poznámky","","","","","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V","(1) - 220 V"]
["","","","","","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V","(2) - 230 V"]
["","","","","","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V","(3) - 240 V"]
["","","","","","(4) - Obsahuje fluórované skleníkové plyny","(4) - Obsahuje fluórované skleníkové plyny","(4) - Obsahuje fluórované skleníkové plyny","(4) - Obsahuje fluórované skleníkové plyny"]
["Štandardné príslušenstvo","Vypúšťacia skrutka","","","","","","1"]
["Ventilátor","Prietok vzduchu","Chladenie","Super nízke","m³/min","","","","","48.9","45.0"]
["","","Kúrenie","Super nízke","m³/min","","","","","43.1","46.3"]
["","","","Super nízke","cfm","","","","","1727","1589"]
["","","Kúrenie","Super nízke","cfm","","","","","1522","1635"]
["Vonkajšie rozmery","Jednotka","","Výška","mm","","","","","735","735"]
["","","","Šírka","mm","","","","","825","825"]
["","","","Hĺbka","mm","","","","","300","300"]
["Hmotnosť","Jednotka","","","kg","","","","","47","48"]
["Motor ventilátora","Rýchlosť","Chladenie","Super nízke","ot/min","","","","","670"]
["","","Kúrenie","Super nízke","ot/min","","","","","670"]
["Kompresor","Typ","","","","","","","","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor"]
["Prevádzkový rozsah","Chladenie","Okolitá teplota","Min.","°CDB","","","","","-10","-10"]
["","","","Max.","°CDB","","","","","46","46"]
["","Kúrenie","Okolitá teplota","Min.","° CWB","","","","","-15","-15"]
["","","","Max.","° CWB","","","","","18","18"]
["Hladina akustického tlaku","Chladenie","","Vysoké","dBA","","","","","48","49"]
["","","","Nízka","dBA","","","","","44","46"]
["","Kúrenie","","Vysoké","dBA","","","","","48","49"]
["","","","Nízka","dBA","","","","","45","46"]
["Chladivo","Typ","","","","","","","","R-410A","R-410A"]
["","Náplň","","","kg","","","","","1.7","1.5"]
["","Náplň","","","tCO2Eq","","","","","3.5","3.1"]
["","GWP","","","","","","","","2087.5","2087.5"]
["Pripojenia potrubí","Dĺžka potrubia","Max.","OU - IU","m","","","","","30","30"]
["","Dodatočná náplň chladiva","","","kg/m","","","","","0,020 (pre potrubie s dĺžkou presahujúcou 10m)","0,020 (pre potrubie s dĺžkou presahujúcou 10m)"]
["","Úroveň hladiny","IU - OU","Max.","m","","","","","20.0","20"]
["Štandardné príslušenstvo","Installation manual","","","","","","","","1","1"]
["","Drain plug","","","","","","","","1","1"]
["Napájanie","Fáza","","","","","","","","1~","1~"]
["Zdroj napájania","Frekvencia","","","Hz","","","","","50","50"]
["","Napätie","","","V","","","","","220-230-240","220-230-240"]
["Poznámky","","","","","","","","","","(1) - 230 V"]