{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":9,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-MV1"]
[]
[]
[]
[]
["","","","","","RZAG71M7V1B","RZAG100M7V1B","RZAG125M7V1B","RZAG140M7V1B"]
["Hladina akustického tlaku","Kúrenie","","Men.","dBA","","","","52"]
["","Chladenie","","Men.","dBA","","","","51"]
["Štandardné príslušenstvo","Upínacie pásy","","","","","","","2"]
["","Návod na montáž","","","","","","","1"]
["","Štítok chladiacej látky pre reguláciu plynu F","","","","","","","1"]
["","Všeobecné bezpečnostné opatrenia","","","","","","","1"]
["","Energetická trieda LOT10","","","","","","","1"]
["Chladiace médium","Charge","","","TCO2Eq","","","","2.53"]
["","GWP","","","","","","","675"]
["","Náplň","","","kg","","","","3.75"]
["","Typ","","","","","","","R-32"]
["Pripojenia potrubia","Kvapalina","","OD","mm","","","","9.52"]
["","Dĺžka potrubia","Max.","OU - IU","m","","","","85"]
["","","Systém","Bez náplne","m","","","","40"]
["","","","Ekvivalentné","m","","","","100"]
["","Plyn","","OD","mm","","","","15.9"]
["","Úroveň hladiny","IU - IU","Max.","m","","","","0.5"]
["","","IU - OU","Max.","m","","","","30.0"]
["","Dodatočná náplň chladiva","","","kg/m","","","","Pozrite si inštalačnú príručku"]
["Sound power level","Chladenie","","","dBA","","","","70"]
["","Vykurovanie","","","dBA","","","","70 (1)"]
["Kompresor","Typ","","","","","","","Hermeticky utesnený kolísavý kompresor"]
["Vonkajšie rozmery","Jednotka","","Šírka","mm","","","","940"]
["","","","Hĺbka","mm","","","","320"]
["","","","Výška","mm","","","","1,430"]
["Hmotnosť","Jednotka","","","kg","","","","92"]
["Power supply","Fáza","","","","","","","1~"]
["","Frekvencia","","","Hz","","","","50"]
["","Napätie","","","V","","","","220-240"]
["Poznámky","","","","","","","","(1) - Podľa ENER Lot 21"]
["","","","","","","","","(2) - Európska/medzinárodná technická norma určujúca limity pre harmonické prúdy generované zariadeniami pripojenými k verejným systémoch s nízkym napätím s príkonom > 16 A a ≤ 75 A na fázu"]
["","","","","","","","","(3) - Ssc: skratový výkon"]
["","","","","","","","","(4) - Európska/medzinárodná technická norma určujúca limity pre harmonické prúdy generované zariadeniami pripojenými k verejným systémoch s nízkym napätím s príkonom ≤ 16 A na fázu."]
["Vonkajšie rozmery","Jednotka","","Výška","mm","990","1430","1430"]
["","","","Šírka","mm","940","940","940"]
["","","","Hĺbka","mm","320","320","320"]
["Hmotnosť","Jednotka","","","kg","70","92","92"]
["Kompresor","Typ","","","","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor"]
["Prevádzkový rozsah","Chladenie","Okolitá teplota","Min.","°CDB","-20","-20","-20"]
["","","","Max.","°CDB","52","52","52"]
["","Kúrenie","Okolitá teplota","Min.","° CWB","-20","-20","-20"]
["","","","Max.","° CWB","18.0","18.0","18.0"]
["Akustický výkon","Chladenie","","","dBA","64","66","69"]
["Hladina akustického tlaku","Chladenie","","Men.","dBA","46","47","50"]
["","Kúrenie","","Men.","dBA","49","51","52"]
["Chladivo","Typ","","","","R-32","R-32","R-32"]
["","Náplň","","","kg","2.95","3.75","3.75"]
["","GWP","","","","675","675","675"]
["","Náplň","","","tCO2Eq","1.99","2.53","2.53"]
["Pripojenia potrubia","Kvapalina","","OD","mm","9.52","9.52","9.52"]
["","Plyn","","OD","mm","15.9","15.9","15.9"]
["Pripojenia potrubí","Dĺžka potrubia","Max.","OU - IU","m","55","85","85"]
["","","Systém","Ekvivalentné","m","75","100","100"]
["","","","Bez náplne","m","40","40","40"]
["","Dodatočná náplň chladiva","","","kg/m","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku"]
["","Úroveň hladiny","IU - OU","Max.","m","30.0","30.0","30.0"]
["","","IU - IU","Max.","m","0.5","0.5","0.5"]
["Štandardné príslušenstvo","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Napájanie","Fáza","","","","1~","1~","1~"]
["Zdroj napájania","Frekvencia","","","Hz","50","50","50"]
["","Napätie","","","V","220-240","220-240","220-240"]
["Istenie – 50 Hz","Maximálne istenie (MFA)","","","A","20","32","32"]
["Akustický výkon","Vykurovanie","","","dBA","","","69 (1)"]
["Poznámky","","","","","","","(1) - Podľa ENER Lot 21"]