{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":13,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NV1"]
[]
[]
[]
[]
["","","","","","RZAG71N7V1B","RZAG71N2V1B","RZAG100N2V1B","RZAG100N7V1B","RZAG125N2V1B","RZAG125N7V1B","RZAG140N2V1B","RZAG140N7V1B"]
["Vonkajšie rozmery","Jednotka","","Výška","mm","870","870","870","870","870","870","870","870"]
["","","","Šírka","mm","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Hĺbka","mm","460","460","460","460","460","460","460","460"]
["Hmotnosť","Jednotka","","","kg","81","81","85","85","95","95","95","95"]
["Kompresor","Typ","","","","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor","Hermeticky utesnený kolísavý kompresor"]
["Prevádzkový rozsah","Chladenie","Okolitá teplota","Min.","°CDB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CDB","52","52","52","52","52","52","52","52"]
["","Kúrenie","Okolitá teplota","Min.","° CWB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","° CWB","18","18","18","18","18","18","18","18"]
["Akustický výkon","Chladenie","","","dBA","64","64","66","66","69","69","70","70"]
["","Vykurovanie","","","dBA","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Hladina akustického tlaku","Chladenie","","Men.","dBA","46","46","47","47","49","49","50","50"]
["","Kúrenie","","Men.","dBA","48","48","50","50","52","52","52","52"]
["Chladivo","Typ","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Náplň","","","kg","3.2","3.20","3.20","3.2","3.70","3.7","3.70","3.7"]
["","GWP","","","","675","675","675","675","675","675","675","675"]
["","Náplň","","","tCO2Eq","2.16","2.16","2.16","2.16","2.50","2.5","2.50","2.5"]
["Pripojenia potrubia","Kvapalina","","OD","mm","10","10","10","10","10","10","10","10"]
["","Plyn","","OD","mm","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["Pripojenia potrubí","Dĺžka potrubia","Max.","OU - IU","m","55","55","85","85","85","85","85","85"]
["","","Systém","Ekvivalentné","m","75","75","100","100","100","100","100","100"]
["","","","Bez náplne","m","40","40","40","40","40","40","40","40"]
["","Dodatočná náplň chladiva","","","kg/m","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku","Pozrite si inštalačnú príručku"]
["","Úroveň hladiny","IU - OU","Max.","m","30","30","30","30","30","30","30","30"]
["","","IU - IU","Max.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Štandardné príslušenstvo","Návod na montáž","","","","1","1","1","1","1","1","1","1"]
["","Štítok chladiacej látky pre reguláciu plynu F","","","","1","1","1","1","1","1","1","1"]
["","Všeobecné bezpečnostné opatrenia","","","","1","1","1","1","1","1","1","1"]
["","Odlepiteľná nálepka F-plyn","","","","1","1","1","1","1","1","1","1"]
["","Upínacie pásy","","","","2","2","2","2","2","2","2","2"]
["Napájanie","Fáza","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["Zdroj napájania","Frekvencia","","","Hz","50","50","50","50","50","50","50","50"]
["","Napätie","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Istenie – 50 Hz","Maximálne istenie (MFA)","","","A","20","20","32","32","32","32","32","32"]
["Poznámky","","","","","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21","(1) - Podľa ENER Lot 21"]